## Exe Summary
Key Phases
| Top- Critical Equipment | Priortity | Vendor Evaluation (Feedback to Acwa BD/PEO) | Fleet Health Index | EPRI PMBD Task Guidelines | MPC | bsolescence Review | Responsibilty Focal Point | Proposed Support | datacollection |  | Support MPC | Support 3rd Party (Health Index) | Support 3rd Party (Scope + Standardization)
|  |  | A | B | P | C | D
1 | Generator | 2 |  | X | X | X |  |  | EPRI Generator Dept | X | Training |  | EPRI (Bill Moore) | Laborelec
| Excitation (collector) | 1 |  |  | X |  | X |  | in-house
2 | Excitation (AVR) | 2 |  |  | X |  | X |  | in-house
3 | Generator Earth Monitoring | 1 |  |  | X |  |  |  | EPRI Generator Dept
4 | Critical Transformer (Step-Up, UAT) | 1 | X | X | X | X |  |  | Laborelec Transformer Dept | X |  |  | datacollection started
5 | Critical Transformer (Excitation) | 1 | X | X | X | X |  |  | Laborelec Transformer Dept | X |  |  | datacollection started
6 | Critical Transformer (PV MV Transfo) | 1 | X | X | X | X |  |  | Laborelec Transformer Dept | X |  |  | datacollection started
7 | HV/MV cables (SPOF) | 1 |  |  | X |  |  |  | in-house | X
8 | HV/MV cable sealing ends (SPOF) | 1 |  |  | X |  |  |  | in-house | X
9 | PV Panel | 2 |  |  | X | X |  |  | in-house
10 | Earthing and Lightning | 1 |  | X | X |  |  |  | Fleet Frame On-Call Contract (Manav,..) | X |  |  | datacollection started
11 | UPS / DC charger | 1 | X | X | X |  | X |  | Fleet Frame On-Call Contract (Statron) | X |  |  | datacollection started
12 | DC Stationary Batteries | 1 |  | X | X |  |  |  | Fleet Frame On-Call Contract (Statron) | X |  |  | datacollection started
13 | Electrical Protections | 2 |  |  | X |  | X |  | Fleet Frame On-Call Contract (helpline)
14 | MV/LV Switchgear (Arc Flash) | 1 |  |  | X |  |  |  | Fleet Frame On-Call Contract |  |  |  | arc flash study on going
15 | Generator Circcuit Breaker (GCB) | 2 |  |  | X |  |  |  | OEM Survey | X
16 | Variable Speed Drive (SPOF/MV systems) | 2 |  |  | X |  | X |  | OEM Survey | X
17 | MV motors | 2 |  |  | X | X |  |  | in-house
18 | CSP Heat Tracing Critical Equipment | 1 |  |  | X |  |  |  | in-house
19 | Transformer (oil) | 1 |  | X | X | X |  |  | Laborelec Oil Dept |  |  |  | sampling Fleet ongoing
20 | Gas Turbine (oil) | 1 |  | X | X | X |  |  | Laborelec Oil Dept |  |  |  | sampling Fleet ongoing
21 | Steam Turbine (oil) | 1 |  | X | X | X |  |  | Laborelec Oil Dept |  |  |  | sampling Fleet ongoing
22 | Critical Pumps | 2 | X |  | X | X |  |  | in-house
23 | Air Compressors | 2 |  |  | X | X |  |  | in-house
24 | Gas Compressors | 2 |  |  | X | X |  |  | in-house
25 | HRSG/Boiler | 1 |  |  | X | X |  |  | Fleet Frame On-Call Contract
26 | Critical Valve Management | 1 | X | X | X | X |  |  | Fleet Frame On-Call Contract | X
27 | Storage Tanks (Molten Salt + other API 650 tanks) | 2 |  |  | X |  |  |  | Fleet Frame On-Call Contract | X |  |  | fleet site survey?
28 | Pressure Vessels | 2 |  |  | X |  |  |  | Fleet Frame On-Call Contract | X |  |  | fleet site survey?
29 | CSP - SGS and TES Heat Exchangers | 1 | X |  | X | X |  |  | in-house | X |  |  | fleet site survey?
30 | Cooling Tower (wet/dry) | 1 | X | X | X | X |  |  | Cooling Tower Contractor (Start Company)
31 | Gas Chromatograph | 2 |  |  | X |  |  |  | Fleet Frame On-Call Contract
32 | HTF Degradation | 2 |  | X |  |  |  |  | in-house
33 | DCS system/Control System | 2 |  |  | X |  | X |  | in-house
34 | RO membranes | 1 | X | X | X | X |  |  | in-house
35 | Wind | 2 | X |  | X | X |  |  | in-house
36 | Critical Plant Instrumentation (Plant Protection/EHS legal) | 1 |  |  | X |  |  |  | in-house
37 | PV Central/String Inverter | 1 |  | X |  |  |  |  | in-house | X
| Systems |  | Vendor Qualification | System Health Assessment | PMBD Alignment | MPC | obsolescence Reviews | Responsibilty Focal Point | Proposed Support
1 | GRP Piping SPOF management | 1 |  |  | X |  |  |  | 3rd Party Validation Check
2 | SPOF Spare Identification and Ordering | 1 | [6 empty] | in-house
3 | Plant Corrosion Review | 2 |  | X | X |  |  |  | Fleet Frame Contract |  |  |  | fleet site survey
4 | Civil Structure Review | 2 |  | X | X |  |  |  | Fleet Frame Contract |  |  |  | fleet site survey
5 | Condition Monitoring Framework | 2 |  |  | X |  |  |  | In-house |  |  |  | guideline in progress
6 | Frame Work In-House/Outsourced implementation | 2 | [6 empty] | In-house
7 | Insurance Compliance | 1 | [6 empty] | In-house
8 | SCD Equipment Test Compliance (cross check PMBD) | 1 |  |  | X |  |  |  | Fleet Frame Contract |  |  |  | PMBD check and complaince cross check with each Planner

## Execution List
| Priority Level High -1 Medium - 2 | Program (Top Critical Equpiment) |  |  | Plant/Region Actions | Comments | Objective Outcome | Main TEch Accountabilty | Tata involvement |  | Recommended 3rd Party Interfaces | Target | Status
1 | 1 | Generator | A B | CCGT, Thermal | Complete Generator Database (as per provided Nomac data template) | Geneator Database (see LL department) | Support in Fleet Health Index, OEM/Model Generator Failure modes (lessons learned),, Business Case for Testing Frame Agreements and Spare Part Pooling | COE/EVP/PGM | X | monitor/track/consolidate |  | Q1 | Open, In Progress, Completed (Traffic Lights)
1 | 2 | Generator | C | CCGT, Thermal | 1)Ensure that all applicable MPC generator alerts are understood, monitored, validated and actioned upon by Plant Operations. 2) Awareness of critical signals, alarms and algorithms (eg. generator stator core temperature) 3)Updating the case management in case of critical alarm |  | 1) Full adoption of MPC 2) Capture of Catches before main degradation/ Failure | EVP/PGM |  |  |  | Q3
1 | 2 | Generator | A B | CCGT, Thermal | Execute Generator Health Index Assessment and Scorecard (as per EPRI Questionnaire) |  | 1) Health Index Rating each Generator, benchmarking 2) Preventive/Predictive Mitigation Actions following the health Index 3) Vendor Qualification Enhancement PEO/BDTS 4) Possible enhancement of O&M plans | COE/EVP/PGM | X | monitor/track/consolidate | EPRI (Bill Moore) | Q3
1 | 2 | Generator | A B | CCGT, Thermal | Technical Letters - TIL/SB completeness and implementation (GE, AES, Siemens). | 1) Red Flag and escalate Critical Open Technical Letters 2) Confirm with respective OEM that all Technical Letters are received and up to date for applicable generators 3) Build Network with same Users in the Region (networking) to assure all lessons learned/TIL completeness | Fleet Generator TIL Compliance Assurance | COE/EVP/PGM |  |  | Respective Users Group OEM Key Account Manager Region | Q4
1 | 1 | Generator | A B | CCGT, Thermal | Ensure Critical Generator Spares Pool Region (per model/type Fleet) | 1) Ensure Critical Spares are available (H2 seals, stator bars, critical consumables like retaining ring liners,.) 2) Set Spare Pooling of strategic Spares Region 3) Validation spare parts stock by EPRI/LBE 4) Preservation strategy on plant generator Haz Mat Consumables | 1) Minimum Generator Spare Part Part Pooling in the Region 2) Identification of external spare part pooling with outside suppliers and vendors (especially haz mat consumables,..) | COE/EVP/PGM |  | monitor and/or consolidate | EPRI and Laborelec | Q2
1 | 2 | Generator | B | CCGT, Thermal | Qualified service supplier contact List + vendor registration [repair and testing capabilities] | 1)Perform a yearly technical evaluation on competency and quality of services 2)Audit Electrical Test Procedures and equipment which Contractor is using. Fleet Standardization Scope and acceptance criteria | Immediate Mobilization capabilty of competent qualified local/regional contractor , especially in case of emergency, Use of approved best practice test standards | COE/EVP/PGM | X | monitor and/or consolidate |  | Q4
1 | 2 | Generator | B | CCGT, Thermal | Electrical Test Equipment Standardization + rationalizaition the Plant/Region | 1) Listing of all available electrical test equipment 2) Confirmation the minimum test equipment is available and rationalized in the Region 3) Calibration Program for each equipment, standardized in place 4) Standardized Validated Test Procedure available for each critical emergency testing 4) People competency on the equipment | 1) Availability of minimum critical test equipment on site and Region for routine and emergency testing (avoid delays of mobilizing external parties, with underperforming equipment) 2) Calibrated and Functional Test Equipment 3) Trained Electrical Team for all critical emergency and routine testing | EVP/PGM | X | monitor and/or consolidate |  | Q4
1 | 2 | Generator | B | CCGT, Thermal | 1)Generator Expertise On-Call Support Contract (remote helpline) 2) Technical scope Contract shall be agreed and aligned with each Region |  | Availability 24/7 days of Generator Expert helpline for emergency | COE/EVP/PGM |  |  | Laborelec | Q3
1 | 2 | Generator | B | CCGT, Thermal | 1) Execute Training Hydrogen-filled Generator Operation 2) Certification of all applicable Operation Team 3) Manual validation (equipment) of H2 purity during every H2 purging and filling cycle. Ensure this is including in the operating site instruction | 1) Only for plants with Hydrogen Cooled Generators | Awareness on Hydrogen Operation Risks and implementation of Best Practices of Hydrogen Filling/Purging | EVP/PGM | X | monitor and/or consolidate | OEM (like EONE) | Q4
2 | 1 | Excitation (Collector) | P | CCGT, Thermal | Ensure compliance EPRI PMBD Guideline Implementation | Auditing | 1)Robust Mitigation to avoid Collector Flash Overs 2) Safety : ensure in no cases a standing rotor earth fault alarm during collector brush maintenance | EVP/PGM | X | spot check field records (remote) | EPRI PMBD/Nomac Guideline | Q2
2 | 1 | Excitation (AVR, Excitation) | A B D | CCGT, Thermal | Ensure Critical Control Cards Spare Pool Region (I/O cards and CPU Cards) available (type/model) |  | 1) Ensure Plant/Regional Spare Parts Pooling in place on typical SPOF excitation Cards for similar plants (AES, Siemens,..) 2) obsolesence | COE/EVP/PGM | X | monitor/consolidate | Fleet Database OEM Review - Spares/Obsolescence | Q2
3 | 1 | Generator Earth Monitoring | P | CCGT, Thermal | Ensure compliance EPRI PMBD Guideline Implementation | Auditing | 1) Rotor Integrity 2) Safety : ensure in no cases a standing rotor earth fault alarm during collector brush maintenance | EVP/PGM | X | spot check field records (remote) | EPRI | Q2
| 1 | Generator Earth Monitoring | B | CCGT, Thermal | Validated Contingency Operation Protocol and Test Protocol in case of rotor earth fault alarm |  |  | COE/EVP/PGM |  |  | EPRI/Laborelec | Q2
4 | 1 | Critical Transformer (including Step Up, Unit Auxiliary | A B | CCGT, Thermal, PV, RO, CSP, Wind | LIVE One Board Transformer Health Oil Dashboard | 1) Mandatory Winter and Summer Oil Campaign by Laborelec | 1) Health Index Rating each Transformer, benchmarking 2) Preventive/Predictive Mitigation Actions following the health Index 3) Vendor Qualification Feedback PEO/BDTS | COE/EVP/PGM | X | monitor and/or consolidate | Laborelec | Q1
4 | 2 | Critical Transformer (including Step Up, Unit Auxiliary | C | CCGT, Thermal, PV, RO, CSP, Wind | 1)Ensure that all applicable MPC transformer alerts are understood, monitored, validated and actioned upon by Plant Operations. 2) Awareness of critical signals, alarms and algorithms (eg. generator stator core temperature) 3)Updating the case management in case of critical alarm |  | 1) Full adoption of MPC 2) Capture of Catches before main degradation/ Failure | EVP/PGM |  |  |  | Q3
4 | 1 | Critical Transformer (including Step Up, Unit Auxiliary | A B | CCGT, Thermal, PV, RO, CSP, Wind | Perform Fleet Health Index Assessment (including Health Index, and Clustering) |  | 1) Health Index Rating each Transformer, benchmarking 2) Preventive/Predictive Mitigation Actions following the health Index 3) Vendor Qualification Feedback PEO/BDTS 4) Possible enhancement of O&M plans | COE/EVP/PGM | X | monitor and/or consolidate | Laborelec | Q2
4 | 1 | Critical Transformer (including Step Up, Unit Auxiliary | A B | CCGT, Thermal, PV, RO, CSP, Wind | Ensure Critical Transformer Spares Pool Region (per model/type Fleet) | 1) Ensure Critical Spares are available (Bucholz,.) 2) Set Spare Pooling of strategic Spares Region 3) Validation spare parts stock 4) Preservation strategy on plant generator Haz Mat Consumables | 1) Minimum Transformer Spare Part Part Pooling in the Region 2) Identification of external spare part pooling with outside suppliers and vendors (eg. Bushings, ..) | COE/EVP/PGM | X | monitor and/or consolidate | EPRI and Laborelec | Q2
4 | 2 | Critical Transformer (including Step Up, Unit Auxiliary | B | CCGT, Thermal, PV, RO, CSP, Wind | Qualified service supplier contact List + vendor registration [repair and testing capabilities] | 1)Perform a yearly technical evaluation on competency and quality of services 2)Audit Electrical Test Procedures and equipment which Contractor is using. Fleet Standardization Scope and acceptance criteria | Immediate Mobilization capabilty of competent qualified local/regional contractor , especially in case of emergency, Use of approved best practice test standards | COE/EVP/PGM | X | monitor and/or consolidate |  | Q4
4 | 2 | Critical Transformer (including Step Up, Unit Auxiliary | B | CCGT, Thermal, PV, RO, CSP, Wind | Electrical Test Equipment Standardization + rationalization for Plant/Region | 1) Listing of all available electrical test equipment 2) Confirmation the minimum test equipment is available and rationalized in the Region 3) Calibration Program for each equipment, standardized in place 4) Standardized Test Procedure available for each critical emergency testing 4) People competency on the equipment | 1) Availability of minimum critical test equipment on site and Region for routine and emergency testing (avoid delays of mobilizing external parties, with underperforming equipment) 2) Calibrated and Functional Test Equipment 3) Trained Electrical Team for all critical emergency and routine testing | EVP/PGM | X | monitor and/or consolidate |  | Q4
| 2 | Critical Transformer (including Step Up, Unit Auxiliary | B | CCGT, Thermal, PV, RO, CSP, Wind | Perform the Training Oil Sampling with signed attendance sheets |  | Correct Sampling leads to correct Results and Analysis | EVP/PGM | X | monitor/track | Laborelec | Q3
| 1 | Excitation Transformer | A B | CCGT, Thermal, CSP | Identify and list all GT/ST excitation transformers + spare pooling business case | Excitation Transformers do have special ratings and not standard available in the Market | 1) Business Case for Spare Pooling each type of Excitation Transformer Region and Fleet + final decision on the need 2) Identification if anhy spare transformers in the fleet | COE/EVP/PGM | X | monitor and/or consolidate |  | Q1
| 1 | PV MV Oil Filled Transformer | A B | PV | Complete PV MV Transfomer Database (as per provided Nomac data template) | Transformer Database | Support in Fleet Health Index, OEM/Model Transformer Failure modes (lessons learned),, Business Case for Testing Frame Agreements and Spare Part Pooling | COE/EVP/PGM | X | monitor and/or consolidate |  | Q1
| 2 | PV MV Oil Filled Transformer | A B | PV | PV MV transfo design checklist - acceptance criteria | [6 empty] | Q3
| 1 | PV MV Oil Filled Transformer | B | PV | Implement the Oil Testing Strategy as per Nomac PV MV TransformerGuidelines (including baseline for New Build) |  | 1) Business Case for Spare Pooling each type of Excitation Transformer 2) Identification of spare transformers in the fleet 3) Vendor Qualification Enhancement | COE/EVP/PGM | X | monitor and/or consolidate | Laborelec | Q1
| 2 | PV MV Oil Filled Transformer | B | PV | Electrical Test Equipment Standardization + rationalization for the Plant/Region | 1) Listing of all available electrical test equipment 2) Confirmation the minimum test equipment is available and rationalized in the Region (incl Harmonic Testing Surveys) 3) Calibration Program for each equipment, standardized in place 4) Standardized Test Procedure available for each critical emergency testing 4) People competency on the equipment | 1) Availability of minimum critical test equipment on site and Region for routine and emergency testing (avoid delays of mobilizing external parties, with underperforming equipment) 2) Calibrated and Functional Test Equipment 3) Trained Electrical Team for all critical emergency and routine testing | EVP/PGM | X | monitor and/or consolidate |  | Q4
5 | 1 | HV/MV Cable System | A B | CCGT, Thermal, PV, RO, CSP, Wind | Identification and Register all Single Point of Failure HV cables and/or MV cables . |  |  | COE/EVP/PGM | X | monitor and/or consolidate | Cable Suppliers/OEM | Q1
| 1 | HV/MV Cable System | A B | CCGT, Thermal, PV, RO, CSP, Wind | Propose and Implement a Rationalized Spare Pool Stock per Region (SPOF cables and/or repair kits) | Internal (Nomac) or preferred external (local cable suppliers) |  | COE/EVP/PGM | X | monitor and/or consolidate | Cable Suppliers/OEM | Q2
5 | 1 | HV/MV Cable System | B | CCGT, Thermal, PV, RO, CSP, Wind | Set On-Call Frame Agreement - Ressources and Repair kits for emergency cable repair |  |  | COE/EVP/PGM |  |  | Cable Suppliers/OEM | Q2
5 | 2 | HV/MV Cable System | B | CCGT, Thermal, PV, RO, CSP, Wind | Electrical Test Equipment Standardization + rationalization the Plant/Region | 1) Listing of all available electrical test equipment 2) Confirmation the minimum test equipment is available and rationalized in the Region 3) Calibration Program for each equipment, standardized in place 4) Standardized Test Procedure available for each critical emergency testing 4) People competency on the equipment | 1) Availability of minimum critical test equipment on site and Region for routine and emergency testing (avoid delays of mobilizing external parties, with underperforming equipment) 2) Calibrated and Functional Test Equipment 3) Trained Electrical Team for all critical emergency and routine testing | EVP/PGM |  |  |  | Q4
5 | 1 | HV/MV Cable System | P | CCGT, Thermal, PV, RO, CSP, Wind | Ensure compliance EPRI PMBD Guideline Implementation | Auditing | Ensure Healthiness of HV cable system | EVP/PGM | X | spot check field records (remote) |  | Q2
| 2 | HV/MV Cable System | B | CCGT, Thermal, PV, RO, CSP, Wind | Ensure annual PD monitoring and trending for HV Cable Joints which are installed on SPOF cable systems (If applicable) | Auditing Calibrated internal Test Equipment available in the Region (if applicable) | Reliable HV cable System | EVP/PGM | X | monitor and/or consolidate |  | Q4
| 1 | HV/MV Cable System | B | CCGT, Thermal, PV, RO, CSP, Wind | Ensure minimum 2 x HV cable Joint Repair Kit available for SPOF cables (especially for ratings equal/above 132kV) | 1)Preservation Strategy to be checked for repair kits 2)Rationalized Spare Pool Holding in Region | Immedidate Repair material availble (for HV ratings) | EVP/PGM | X | monitor and/or consolidate |  | Q2
| 1 | HV/MV Cable Sealing Ends (CSE) | A B | CCGT, Thermal, PV, RO, CSP, Wind | DataBase of all HV cable sealings on all SPOF HV/MV cable systems |  | 1) Ensure SPOF spare available by hand - intenal Nomac or external Supplier/OEM in the Fleet (Cable Sealing Ends) 2) Vendor Qualifcation Enhancement and Standardization CSE for New Build Projects | COE/EVP/PGM | X | monitor and/or consolidate |  | Q1
| 1 | HV/MV Cable Sealing Ends (CSE) | B | CCGT, Thermal, PV, RO, CSP, Wind | Ensure Critical SPOF Spares available for each type CS (Spare Pooling Fleet and/or OEM) |  | 1) Ensure SPOF spare available by hand - intenal Nomac or external Supplier/OEM in the Fleet (Cable Sealing Ends) | COE/EVP/PGM | X | monitor and/or consolidate | Cable Suppliers/OEM | Q2
6 | 2 | PV Panel | A B D | PV | Implementation Nomac PV Panel Degradation Test Procedure (New Build and Operational Plants) |  | 1) Fleet Health Index and Performance 2) Vendor Qualifcation Enhancement | COE/EVP/PGM |  |  |  | Q3
7 | 2 | Earthing and Lightning | B | CCGT, Thermal, PV, RO, CSP, Wind | Execution a 3rd party survey on the overall Plant (Power, BOP, Water) | 1) For Wind, this includes the Substation + each separate Wind Mill system | Safety and Plant Availability | EVP/PGM | X | monitor and/or consolidate |  | Q4
| 2 | Earthing and Lightning | B | CCGT, Thermal, PV, RO, CSP, Wind | Set Regional/Fleet Frame Agreement with Approved Standardized Technical Scope |  | Safety and Plant Availability | COE/EVP/PGM |  |  |  | Q4
| 2 | Earthing and Lightning | B | CCGT, Thermal, PV, RO, CSP, Wind | Confirm Methodology "Fall of Potential" and/or Injection (step/touch) in case of technical concern or earth grid modifications |  | Safety and Plant Availability | EVP/PGM |  |  |  | Q4
| 2 | Earthing and Lightning | B | CCGT, Thermal, PV, RO, CSP, Wind | Validation that all site tests, acceptance criteria and results shall be in compliance with IEEE 80 acceptance criteria and local regulations criteria (whichever is most stringent) |  | Safety and Plant Availability | EVP/PGM | X | spot check field records (remote) | 3rd Party Expert Company | Q4
| 2 | Earthing and Lightning | B | CCGT, Thermal, PV, RO, CSP, Wind | Remedial Execution and Closure of all the Critical Non-Compliance to meet the acceptance criteria |  | Safety and Plant Availability | EVP/PGM |  |  |  | Q4
8 | 1 | UPS & DC System (incl. Stationary Batteries and GT/ST Batteries) | A B | CCGT, Thermal, PV, RO, CSP, Wind | Set Fleet Database Batteries (VRLA /NiCD) , applied for UPS and DC Charger |  |  | COE/EVP/PGM | X | monitor and/or consolidate | STATRON | Q1
| 1 | UPS & DC System (incl. Stationary Batteries and GT/ST Batteries) | A B | CCGT, Thermal, PV, RO, CSP, Wind | Set Fleet Review of all installed AC/DC capacitors | Confirm Suitable Application and Lifetime and compliance to Ambient Temperature as per Spec | Mitigate Fire Risks and Low Quality Capacitors | COE/EVP/PGM | X | monitor and/or consolidate |  | Q1
| 1 | UPS & DC System (incl. Stationary Batteries and GT/ST Batteries) | P | CCGT, Thermal, PV, RO, CSP, Wind | Ensure compliance EPRI PMBD Guideline Implementation Batteries VRLA and NICd type | Including Yearly Discharge Testing all VRLA types | Assure Battery Healthiness and Performance | EVP/PGM | X | spot check field records (remote) |  | Q2
| 1 | UPS & DC System (incl. Stationary Batteries and GT/ST Batteries) | P | CCGT, Thermal, PV, RO, CSP, Wind | Ensure compliance EPRI PMBD Guideline Implementation Capacitors | Including regular thermography and condensator measurements) and 5 Years replacement schedule | Mitigate Fire Risks and Low Quality Capacitors | EVP/PGM | X | spot check field records (remote) |  | Q2
8 | 1 | UPS & DC System (incl. Stationary Batteries and GT/ST Batteries) | A B | CCGT, Thermal, PV, RO, CSP, Wind | SPOF review on UPS /DC systems |  |  | COE/EVP/PGM | X | monitor and/or consolidate |  | Q1
8 | 1 | UPS & DC System (incl. Stationary Batteries and GT/ST Batteries) | A B D | CCGT, Thermal, PV, RO, CSP, Wind | UPS and Battery Health Index Assessment |  | 1) Health Index Rating each UPS and Batteries, benchmarking 2) Preventive/Predictive Mitigation Actions following the health Index 3) Vendor Qualification Enhancement PEO/BDTS 4) Obsolescence | COE/EVP/PGM | X | monitor and/or consolidate | 3rd Party (eg,Statron) | Q2
8 | 1 | UPS & DC System (incl. Stationary Batteries and GT/ST Batteries) | B | CCGT, Thermal, PV, RO, CSP, Wind | Set Regional/Fleet Frame Agreement Batteries with Approved Standardized Technical Scope | 1) Standardized + Validated Test Procedure available for battery discharge Testing. 2) Acceptance Criteria standaridzed and as per IEC standards | Standardized Test Methodoloy and Fleet Healthiness Battery Systems | COE/EVP/PGM | X | monitor and/or consolidate | 3rd Party (eg,Statron) | Q2
| 1 | UPS & DC System (incl. Stationary Batteries and GT/ST Batteries) | B | CCGT, Thermal, PV, RO, CSP, Wind | Set Regional/Fleet Frame Agreement UPS maintenance and Testing with Approved Standardized Technical Scope | 1) Standardized + Validated Test Procedure available (incl change over testing) 2) Acceptance Criteria standaridzed and as per IEC standards | Standardized Test Methodoloy and Fleet Healthiness UPS Systems | COE/EVP/PGM | X | monitor and/or consolidate | 3rd Party (eg,Statron) | Q2
9 | 1 | Electrical Protections (Critical Transformer Step Up and UAT, MV/LV switchgear, Generator) | A B | CCGT, Thermal, PV, RO, CSP, Wind | Set Fleet Database Critical Protections (as per provided Nomac template) | 1) OEM, Models, Application, Number installed, Year of Commissioning,.. | Obsolescence Review Vendor Qualification Enhancement Review feasability frame agreement Testing | COE/EVP/PGM | X | monitor and/or consolidate |  | Q1
9 | 2 | Electrical Protections (Critical Transformer Step Up and UAT, MV/LV switchgear, Generator) | A B D | CCGT, Thermal, PV, RO, CSP, Wind | Equipment Fleet Review by respective OEM to confirm any obsolescence and/or Technical Letters |  | Obsolescence Review Vendor Qualification Enhancement Review feasability frame agreement Testing | COE/EVP/PGM |  |  |  | Q3
9 | 2 | Electrical Protections (Critical Transformer Step Up and UAT, MV/LV switchgear, Generator) | B | CCGT, Thermal, PV, RO, CSP, Wind | Set electrical Protection On-Call Support Contract (helpline) [for affected plants) | 1) For Protection Selectivity Reviews in case of major plant /unit disturbances in the past 1 year 2022 | Obsolescence Review Vendor Qualification Enhancement Review feasability frame agreement Testing | EVP/PGM |  |  | 3rd Party (eg,Engie, DNV,..) | Q4
10 | 2 | MV/LV SwitchBoard | B | CCGT, Thermal, PV, RO, CSP, Wind | Arc Flash Study and Implementation for all New Buld and Operational Plants |  | Safety and Availability | COE/EVP/PGM | X | monitor and/or consolidate | 3rd Party (eg, TUV) | Q4
10 | 2 | MV/LV SwitchBoard | B | CCGT, Thermal, PV, RO, CSP, Wind | Validate all " EPC executed" Arc Flash Studies (New build) by expert |  | Assure EPC methodology, and acceptance criteria is in line with Nomac approved Guideline Safety and Availability | COE/EVP/PGM |  |  | 3rd Party (eg, TUV) | Q4
| 2 | MV/LV SwitchBoard | B | CCGT, Thermal, PV, RO, CSP, Wind | All Arc Flash Recommendations (incl. signage, training, PPE, and mitigations to reduce arc energy) are implemented. |  | Safety and Availability | EVP/PGM |  |  | 3rd Party (eg, TUV) | Q4
| 2 | MV/LV SwitchBoard | B | CCGT, Thermal, PV, RO, CSP, Wind | High Humidity Problems and Rain Ingress in the Room shall be notifified and attended immediately in each Electrical Room on site | Excessive high Humidity = condensation of moisture on the Switchgear surfaces | Safety and Availability : avoid Shorts and Flash Overs | EVP/PGM |  |  |  | Q4
11 | 1 | Generator Circuit Breaker | A B | CCGT, Thermal, CSP | Set dataBase (as per provided Nomac data template) |  | Support in Fleet Health Index, OEM/Model Generator Failure modes (lessons learned),, Business Case for Testing Frame Agreements and Spare Part Pooling | COE/EVP/PGM | X | monitor and/or consolidate | OEM (ABB, GE,..) | Q1
11 | 1 | Generator Circuit Breaker | A B | CCGT, Thermal, CSP | Ensure Critical GCB spares Pool Region (per model/type Fleet) | 1) Ensure Critical Spares are available (incl Voltage Transformer, Oil Pump , ) 2) Set Spare Pooling of strategic Spares Region | 1) Minimum GCB Spare Part Part Pooling in the Region 2) Identification of external spare part pooling with outside suppliers and vendors (especially haz mat consumables,..) 3) Idendification of available GCB /GCB spares in the Fleet | COE/EVP/PGM | X | monitor and/or consolidate | OEM (ABB, GE,..) | Q2
| 2 | Generator Circuit Breaker | A B | CCGT, Thermal, CSP | identification and implementation of technical letters and technical reliaibility recommendation from OEM |  |  | COE/EVP/PGM |  |  | OEM (ABB, GE,..) | Q4
12 | 1 | Variable Speed Drive (VFD) Critical Equipment | A B | CCGT, Thermal, RO, CSP | Set Fleet Database (template) VFD systems (incl model/type of capacitors) |  | Support in Fleet Health Index, OEM/Model Generator Failure modes (lessons learned),, Business Case for Testing and Maintenance Frame Agreements and Spare Part Pooling | COE/EVP/PGM | X | monitor and/or consolidate | OEM (ABB, GE,..) | Q1
12 | 1 | Variable Speed Drive (VFD) Critical Equipment | B | CCGT, Thermal, RO, CSP | 1)Confirm the quality of the installed AC/DC capacitors with OEM. 2)Confirm the make/model, lifetime and suitability to ambient conditions. |  |  | COE/EVP/PGM | X | monitor and/or consolidate | OEM (ABB, GE,..) | Q1
12 | 2 | Variable Speed Drive (VFD) Critical Equipment | A B D | CCGT, Thermal, RO, CSP | Equipment Fleet Review by respective OEM (incl Obsolescence/ technical letters) |  |  | COE/EVP/PGM | X | monitor and/or consolidate | OEM (ABB, GE,..) | Q3
12 | 2 | Variable Speed Drive (VFD) Critical Equipment | B | CCGT, Thermal, RO, CSP | Implementation VFD On-Call Support Contract (helpline) |  |  | EVP/PGM |  |  | OEM (ABB, GE,..) | Q3
12 | 2 | Variable Speed Drive (VFD) Critical Equipment | B | CCGT, Thermal, RO, CSP | Training on Troubleshooting VFD probems Signed off sheets |  |  | EVP/PGM | X | monitor and/or consolidate | OEM (ABB, GE,..) | Q3
| 1 | Variable Speed Drive (VFD) Critical Equipment | A B | CCGT, Thermal, RO, CSP | Ensure Critical VFD Spares Pool Region (per model/type Fleet) | 1) Ensure Critical Spares are available ( 2) Set Spare Pooling of strategic Spares Region 3) Validation spare parts | 1) Minimum VFD Spare Part Part Pooling in the Region 2) Identification of external spare part pooling with outside suppliers and vendors (especially haz mat consumables,..) | COE/EVP/PGM | X | monitor and/or consolidate | OEM (ABB, GE,..) | Q2
14 | 2 | MV Motor | B | CCGT, Thermal, RO, CSP | Qualified service supplier contact List + vendor registration [repair and testing capabilities] | 1)Perform a yearly technical evaluation on competency and quality of services 2)Audit Electrical Test Procedures and equipment which Contractor is using. Fleet Standardization Scope and acceptance criteria | 1) Immediate Mobilization capabilty of competent qualified local/regional contractor , especially in case of emergency, Use of approved best practice test standards | COE/EVP/PGM | X | monitor and/or consolidate |  | Q4
| 1 | MV Motor | P | CCGT, Thermal, RO, CSP | Ensure compliance EPRI PMBD Guideline Implementation Motors (including vibration monitoring and temperature monitoring bearings) |  | 2) Best Practice Predictive Monitoring Healthiness | EVP/PGM | X | spot check field records (remote) |  | Q2
15 | 1 | Gas Turbine | A B | CCGT | Turbine LIVE Oil Dashboard (Lube, Hydraulic) | 1) Quarterly Sampling and Testing by certificed Lab 2) For New Build Plants - baseline to be established adn send to Laborelec |  | COE/EVP/PGM | X | monitor and/or consolidate | Laborelec | Q1
| 2 | Gas Turbine | C | CCGT | 1)Ensure that all applicable MPC turbine alerts are understood, monitored, validated and actioned by Plant Operations. 2) Awareness of critical signals, alarms and algorithms 3)Updating the case management in case of critical alarm |  | 1) Full adoption of MPC 2) Capture of Catches before main degradation/ Failure | EVP/PGM | X | track signed TB sheets |  | Q3
15 | 2 | Gas Turbine | A B | CCGT | Technical Letters - TIL/SB completeness and implementation (GE, AES, Siemens,..). | 1) Red Flag and escalate Critical Open Technical Letters 2) Confirm with respective OEM that all Technical Letters are received and up to date for applicable turbines 3) Build Network with same Users in the Region (networking) to assure all lessons learned/TIL completeness | Fleet Turbine TIL Compliance Assurance | COE/EVP/PGM |  |  | EPRI (validation) and OEM | Q4
15 | 1 | Gas Turbine | B | CCGT | Monthly Emergency DC Pump Change-Over Testing and Compliance | 1) Activate the Oil Pressure Switch on Oil Header and Confirm Operation DC Pump for 15 minutes with measurement of the current (as per nameplate) | Reliability Assurance / Insurance | EVP/PGM | X | monitor and/or consolidate |  | Q2
| 1 | Gas Turbine | B | CCGT | Annual Overspeed Testing Performed (to be reconfirmed with OEM in writing) |  | Reliability Assurance / Insurance / Safety | EVP/PGM | X | monitor and/or consolidate | OEM | Q2
16 | 1 | Steam Turbine | A B | CCGT, Thermal, CSP | Turbine LIVE Oil Dashboard (Lube, Hydraulic) | 1) Quarterly Sampling and Testing by certificed Lab 2) For New Build Plants - baseline to be established adn send to Laborelec |  | COE/EVP/PGM | X | monitor and/or consolidate | Laborelec | Q1
| 2 | Steam Turbine | C | CCGT, Thermal, CSP | 1)Ensure that all applicable MPC Turbine screens/dashboard are monitored, validated and actioned upon by Plant Operations. 2) Awareness of critical signals, alarms and algorithms ) 3)Updating the case management in case of critical alarm |  | 1) Full adoption of MPC 2) Capture of Catches before main degradation/ Failure | EVP/PGM | X | track signed TB sheets |  | Q3
16 | 2 | Steam Turbine | A B | CCGT, Thermal, CSP | Technical Letters - TIL/SB completeness and implementation (GE, AES, Siemens, SKODA,..). | 1) Red Flag and escalate Critical Open Technical Letters 2) Confirm with respective OEM that all Technical Letters are received and up to date for applicable turbines 3) Build Network with same Users in the Region (networking) to assure all lessons learned/TIL completeness | Fleet Turbine TIL Compliance Assurance | COE/EVP/PGM |  |  | EPRI (validation) and OEM | Q4
16 | 1 | Steam Turbine | B | CCGT, Thermal, CSP | Monthly Emergency DC Pump Change-Over Testing and Compliance | 1) Activate the Oil Pressure Switch on Oil Header and Confirm Operation DC Pump for 15 minutes with measurement of the current (as per nameplate) | Reliability Assurance / Insurance | EVP/PGM | X | spot check field records (remote) |  | Q2
16 | 1 | Steam Turbine | B | CCGT, Thermal, CSP | Monthly ST Stop and Control (MSCV) Valve Stroking (to be confirmed with OEM in writing) | 1) In compliance with respective OEM guideline (eg. For Siemens STG , this is monthly) 2) Records availabe | Reliability Assurance / Insurance | EVP/PGM | X | spot check field records (remote) |  | Q2
17 | 2 | Critical Pumps (RO, Centrifugal, Vertical , CSP Salt/HTF pumps) | B | CCGT, Thermal, CSP, RO | Qualified service supplier contact List + vendor registration [repair and testing capabilities] | 1)Perform a yearly technical evaluation on competency and quality of services 2)Audit Mechanical Test Procedures and equipment which Contractor is using. Fleet Standardization Scope and acceptance criteria | 1) Immediate Mobilization capabilty of competent qualified local/regional contractor , especially in case of emergency, Use of approved best practice test standards | COE/EVP/PGM | X | monitor and/or consolidate | OEM / 3rd Party | Q4
17 | 2 | Air Compressors and Main Gas Compressors | B | CCGT, Thermal, CSP,RO | Qualified service supplier contact List + vendor registration [repair and testing capabilities] | 1)Perform a yearly technical evaluation on competency and quality of services 2)Audit Mechanical Test Procedures and equipment which Contractor is using. Fleet Standardization Scope and acceptance criteria | 1) Immediate Mobilization capabilty of competent qualified local/regional contractor , especially in case of emergency, Use of approved best practice test standards | COE/EVP/PGM | X | monitor and/or consolidate | OEM | Q4
| 1 | Main Gas Compressors | A B | CCGT | LIVE Oil Dashboard | 1) Yearly minimum 1 x Oil Sample to be send to Laborelec 3) New Build Plants - baseline to be send to Laborelec |  | COE/EVP/PGM | X | monitor and/or consolidate | Laborelec | Q1
18 | 1 | HRSG/Boiler | B | CCGT, Thermal, CSP | Chemistry Site Review and implementation of all recommmendations |  | Best Practice Operation and Dosing implementation | EVP/PGM |  |  | Marc Dewispeleare | Q1 | pending Hassyan, Dewa CSP, Sidarya
18 | 2 | HRSG/Boiler | A B | CCGT, Thermal, CSP | LIVE Chemistry Dashboard | 1) Chemistry Dashboard LIVE on a dedicated Screen in the Control Room 2) Signed Toolbox Form including each CCR Operator |  | COE/EVP/PGM |  |  | Marc Dewispeleare | Q4
18 | 2 | HRSG/Boiler | B | CCGT, Thermal, CSP | Execution FAC Study with identificaiton of all Risk Areas on High Pressure piping |  | Safety /Availiabilty High Pressure Piping | COE/EVP/PGM |  |  | Marc Dewispeleare | Q4
| 2 | HRSG/Boiler | B | CCGT, Thermal, CSP | Define and Implement the Inspection Strategy (eg. NDT tests/Thickness Test ) based on the FAC report recommendations |  | Safety /Availiabilty High Pressure Piping | COE/EVP/PGM |  |  |  | Q4
| 2 | HRSG/Boiler | B | CCGT, Thermal, CSP | Ensure the Inspection Strategy is uploaded in SAP and scheduled accordingly |  | Safety /Availiabilty High Pressure Piping | EVP/PGM |  |  |  | Q4
18 | 1 | HRSG/Boiler | B | CCGT, Thermal, CSP | On-Call Support Contract Chemistry Fleet in place |  | Availability 24/7 days of Generator Expert helpline for emergency. | EVP/PGM |  |  | Marc Dewispeleare | Q1 | only MEA region, to be done for Fleet
| 2 | HRSG/Boiler | B | CCGT, Thermal, CSP | Validation Analyzers equimpent for SWAS system is Available in each Plant |  | Reliabilty of SWAS measurements | EVP/PGM |  |  |  | Q3 | equipment delivery KSA
| 2 | HRSG/Boiler | B | CCGT, Thermal, CSP | Validation Program SWAS Equipment is in place as per Nomac Guideline (i.e pH and conductivity validation minimum weekly) |  | Reliabilty of SWAS measurements | EVP/PGM |  |  |  | Q3 | equipment delivery KSA
19 | 1 | Critical Valve Management (HRSG, BOP, GT) | B | CCGT, Thermal, CSP, | Execute Criticality Ranking - especially on all plant performance related Valves |  | Enhance Plant Performance | EVP/PGM | X | monitor and/or consolidate |  | Q2
19 | 1 | Critical Valve Management (HRSG, BOP, GT) | B | CCGT, Thermal, CSP | Check the site performance of each critical valve (A) on leaking, passing,.. | Use Condition Monitoring Program (Ultra Sonic Testing) | Enhance Plant Performance | EVP/PGM | X | monitor and/or consolidate |  | Q2
| 2 | Critical Valve Management (HRSG, BOP, GT) | A B | CCGT, Thermal, CSP | Ensure a minimum stock for all critical drain valves (other performance affected valves) which have high risk for passing and leaking |  | Enhance Plant Performance | EVP/PGM |  |  |  | Q3
19 | 1 | Critical Valve Management (HRSG, BOP, GT) | B | CCGT, Thermal, CSP | Follow and Implement the Nomac Valve Guideline (made by OEM AVS) for valve replacement | Nomac Guideline include the recommneded valves and types for each application | Enhance Plant Performance | EVP/PGM |  |  |  | Q2
| 1 | Critical Valve Management (HRSG, BOP, GT) | B | CCGT, Thermal, CSP | Ensure a local/regional frame agreement (NMES and Local Contractor) for valve repair , consumables and replacement work |  | Enhance Plant Performance | EVP/PGM |  |  |  | Q2
20 | 2 | Cooling Tower (Wet/Air-Cooled Type) | B | CCGT, CSP | Execute 3rd Party Site Assessment /Site Visit (incl vibrations, installation, water quality, integrity check, spares availability) |  | Assure Cooling Tower Healtiness Enhancement of the O&M Strategy (if applicable)x Awareness on Failure Modes | EVP/PGM |  |  | 3rd Party (StarPower) | Q3
| 2 | Cooling Tower (Wet/Air-Cooled Type) | C | CCGT, CSP | 1)Ensure that all applicable MPC Cooling Tower alerts monitored, validated and actioned upon by Plant Operations. 2) Awareness of critical signals, alarms and algorithms ) 3)Updating the case management in case of critical alarm |  | 1) Full adoption of MPC 2) Capture of Catches before main degradation/ Failure | EVP/PGM | X | track signed TB sheets |  | Q3
| 2 | Cooling Tower Cooling Tower (Wet Type) | B | CCGT, CSP | Execute the minimum checks 1)Review and validation of the hydraulic Balance 2)Analyze the Nozzle connection arrangement and clamping 3)Analyze the drift eliminators & fills integrity and installation |  | Assure Cooling Tower Healtiness Enhancement of the O&M Strategy (if applicable)x Awareness on Failure Modes | EVP/PGM |  |  | 3rd Party (StarPower) | Q3
| 2 | Cooling Tower Cooling Tower (Wet Type) | P | CCGT, CSP | Make a Reviewed/Enhanced PMBD Guideline on Cooling Tower (dry/wet |  | Assure Cooling Tower Healtiness Enhancement of the O&M Strategy (if applicable)x Awareness on Failure Modes | COE/EVP/PGM |  |  |  | Q3
21 | 1 | Storage Tanks i.e. Molten Salt and other API 650 Tanks (Water, Fuel, Oil) | P | CCGT, Thermal, CSP, RO, PV | Develop and issue a Fleet Nomac Inspection Strategy for Internal /External Inspection, according to the fluid, in line with API and local regulations (whatever is most stringent) |  | Legal Compliance /Insurance / Safety and Availability | COE/EVP/PGM |  |  | EPRI / 3rd Party (eg Velosi) | Q2
| 1 | Storage Tanks i.e. Molten Salt and other API 650 Tanks (Water, Fuel, Oil) | B | CCGT, Thermal, CSP, RO, PV | Identify a 3rd party for validation of the inspection strategy and set frame agreement |  | Standardized Test Methodoloy and Fleet Healthiness Pressure Vessel Systems | COE/EVP/PGM |  |  | 3rd Party | Q2
21 | 2 | Storage Tanks i.e. Molten Salt and other API 650 Tanks (Water, Fuel, Oil) | B | CCGT, Thermal, CSP, RO, PV | Implement standardized Regional/Fleet O&M strategy on the applicable Storage Tanks |  |  | EVP/PGM | X | monitor and/or consolidate | EPRI | Q4
21 | 1 | Pressure Vessels (ASME section 8) | P | CCGT, Thermal, CSP, RO | Develop and issue a Fleet Nomac Inspection Strategy for Internal /External Inspection, according to the fluid, in line with API and local regulations (whatever is most stringent) |  | Legal Compliance /Insurance / Safety and Availability | COE/EVP/PGM |  |  | EPRI /3rd Party (eg. J Britt) | Q2
21 | 1 | Pressure Vessels (ASME section 8) | B | CCGT, Thermal, CSP, RO | Set Regional/Fleet Frame Agreement Pressure Vessel maintenance and Testing with Approved Standardized Technical Scope | 1) Standardized + Validated Test Procedure available (incl change over testing) 2) Acceptance Criteria standaridzed and as per IEC standards | Standardized Test Methodoloy and Fleet Healthiness Pressure Vessel Systems | COE/EVP/PGM |  |  | 3rd Party | Q2
| 2 | Pressure Vessels (ASME section 8) | B | CCGT, Thermal, CSP, RO | Implement standardized Regional/Fleet O&M strategy on the applicable Pressure Vessels |  |  | EVP/PGM | X | monitor and/or consolidate |  | Q4
| 1 | CSP - SGS and TES Heat Exchangers | P | CSP | Develop and issue a Fleet Nomac Inspection Strategy for Internal /External Inspection, according to the fluid, in line with API and local regulations (whatever is most stringent) |  | Legal Compliance /Insurance / Safety and Availability | COE/EVP/PGM |  |  | EPRI / 3rd Party | Q2
| 1 | CSP - SGS and TES Heat Exchangers | B | CSP | Set Regional/Fleet Frame Agreement Pressure Vessel maintenance and Testing with Approved Standardized Technical Scope | 1) Standardized + Validated Test Procedure available (incl change over testing) 2) Acceptance Criteria standaridzed and as per IEC standards | Standardized Test Methodoloy and Fleet Healthiness HX Systems | COE/EVP/PGM |  |  |  | Q2
| 2 | CSP - SGS and TES Heat Exchangers | B | CSP | Implement standardized Regional/Fleet O&M strategy on the applicable HX. |  |  | EVP/PGM | X | monitor and/or consolidate |  | Q4
| 2 | CSP - Heat Tracing Critical Equipment | P | CSP | Develop and implement a robust heat tracing inspection and maintenance strategy (on molten-salt equipment) |  | Assure Reliability of the Heat Tracing on the Salt Systems | COE/EVP/PGM | X | monitor and/or consolidate |  | Q4
22 | 1 | Gas Chromotogrraph | P | CCGT | Ensure compliance EPRI PMBD Guideline Implementation |  |  | EVP/PGM | X | spot check field records (remote) |  | Q2
| 2 | Gas Chromotogrraph | B | CCGT | Set On-Call Regional Frame Agreement for an annual maintenance and emergency repair |  |  | EVP/PGM |  |  | OEM (eg. Emerson | Q4
23 | 2 | HTF Degradation Analysis | B | CSP | Development and Implementation of Fleet Standardized Tracker for HTF quality monitoring |  | Assure HTF quality and Plant performance | COE/EVP/PGM |  |  |  | Q4
25 | 2 | DCS System/ Control Systems (PLC , Controllers) | A B D | CCGT, Thermal, RO, CSP, | For all DCS systems , PLC Systems, HMI systems: 1) Identify and Register the Obsolescence Risk per Plant 2) Ensure a Risk Assessment and Mitigation Plan for each |  | Availabilty of the System | COE/EVP/PGM |  |  |  | Q4
26 | 2 | RO Membrane (Demin, RO Plant,..) | B | RO | Assure Normalization Software available and analyzed on weekly basis. | including all systems having Membrances (incl Demin Plant) | Assure Membrane Performance | EVP/PGM |  |  |  | Q4 | Acwa Power RO Track
| 2 | RO Membrane (Demin, RO Plant,..) | B | RO | Assure Membrane Mapping on monthlhy basis (conductivity) , are within acceptance criteria | including all systems having Membrances (incl Demin Plant) | Assure Water Quality | EVP/PGM |  |  |  | Q3
26 | 2 | RO Membrane (Demin, RO Plant,..) | B | RO | Develop and Implement an approved Membrane Replacement Strategy Plan | including all systems having Membrances (incl Demin Plant) | Assure Membrane Performance and optimized replacement cost | COE/EVP/PGM |  |  |  | Q4
| 2 | RO Membrane (Demin, RO Plant,..) | B | RO | Confirm Chemical dosing wihtin the design acceptance criteria | including all systems having Membrances (incl Demin Plant) | Assure Chemical Supply | EVP/PGM |  |  |  | Q3
27 | 2 | WIND | P | Wind | Develop Condition Based Maintenance Strategy |  | Development of robust Condition Based Maintenance for WIND | COE/EVP/PGM |  |  |  | Q4
27 | 2 | WIND | B | Wind | Identify and implement Predictive Maintenance Plan to mitigate the most impactful faults and warnings, from SCADA/ARUNA |  | Development of robust Condition Based Maintenance for WIND | COE/EVP/PGM |  |  |  | Q4
| 2 | WIND | B | Wind | Define and Implement an Inspection Plan for all major Wind equipment (incl. blades , drive train alignement, endoscopies,..) |  | Development of robust Condition Based Maintenance for WIND | COE/EVP/PGM |  |  |  | Q4
28 | 2 | Critifcal Plant Instrumentation (related to Plant Protections or Legal EHS Requirements) | B | CCGT, Thermal, PV, RO, CSP, Wind | Making the Plant Protection List (for each critical equipment A |  | Availability / Assurance Reliability and functionality of the Critical Instrumenents / Safety | EVP/PGM | X | monitor and/or consolidate |  | Q3
| 2 | Critifcal Plant Instrumentation (related to Plant Protections or Legal EHS Requirements) | B | CCGT, Thermal, PV, RO, CSP, Wind | Implement Standardized Plant Procedure including calibration methodology, functional testing and frequency of testing |  | Availability / Assurance Reliability and functionality of the Critical Instrumenents / Safety | EVP/PGM | X | monitor and/or consolidate |  | Q3
28 | 2 | Critifcal Plant Instrumentation (related to Plant Protections or Legal EHS Requirements) | B | CCGT, Thermal, PV, RO, CSP, Wind | Particular for Performance Equipment and Billing Equipment -Implement Standardized PLant Procedure including calibration |  | Availability / Assurance Reliability and functionality of the Critical Performance and Billing instrumentation | EVP/PGM | X | monitor and/or consolidate |  | Q3
| 1 | PV Central/Sring Inverter | A B D | PV | Set Fleet Database (as per provided Nomac template) | 1) OEM, Models, Application, Number installed, Year of Commissioning,.. | Obsolescence Review Vendor Qualification Enhancement Review feasability frame agreement Testing | EVP/PGM | X | monitor and/or consolidate |  | Q1
| 2 | PV Central/Sring Inverter | A | PV | Vendor Qualification Enhancement |  | Standardization - Ambient Temperature to be defined explicitely in the Clauses |  |  |  |  | Q4
| 1 | GRP Critical Piping (RO systems, SW intake, CCW lines,...) | B | CCGT, Thermal, RO | SPOF Risk Assesment Study on all critical GRP systems in each Plant critical system (SW intake, CCW, RO,..) |  | Assure Robust Contigency Plant for Critical GRP pipe leakage | COE/EVP/PGM | X | track |  | Q1
| 1 | GRP Critical Piping (RO systems, SW intake, CCW lines,...) | B | CCGT, Thermal, RO | Involve 3rd Party for Review and Risk Assessment and SPOF Spares recommendation. |  | Assure Robust Contigency Plant for Critical GRP pipe leakage | EVP/PGM |  |  | Same 3rd Party as Hassyan | Q1
| 1 | GRP Critical Piping (RO systems, SW intake, CCW lines,...) | B | CCGT, Thermal, RO | Marked As-Built P&D Drawings (location risk areas, and applicable SPOF GRP spares) |  | Assure Robust Contigency Plant for Critical GRP pipe leakage | EVP/PGM | X | monitor and/or consolidate |  | Q1
| 1 | GRP Critical Piping (RO systems, SW intake, CCW lines,...) | A B D | CCGT, Thermal, RO | 1) SPOF critical spares selection + rationalization review across the Region/Fleet 2) Assess Fleet Spare Pooling(internal Nomac or external with GRP service supplier) |  | Assure Robust Contigency Plant for Critical GRP pipe leakage | COE/EVP/PGM |  |  |  | Q1
| 1 | GRP Critical Piping (RO systems, SW intake, CCW lines,...) | B | CCGT, Thermal, RO | All SPOF GRP spares are ordered and received on site (incl internal sealing GRP parts) |  | Assure Robust Contigency Plant for Critical GRP pipe leakage | EVP/PGM |  |  |  | Q1
| 1 | GRP Critical Piping (RO systems, SW intake, CCW lines,...) | B | CCGT, Thermal, RO | GRP Regional On-Call Support Contract (ressources, consumables, approved repair protocol) | 1)Perform a yearly technical evaluation on competency and quality of services 2)Audit Test/Repair tProcedures and equipment which Contractor is using. Fleet Standardization Scope and acceptance criteria | Assure Robust Contigency Plant for Critical GRP pipe leakage | COE/EVP/PGM |  |  |  | Q1
| 1 | GRP Critical Piping (RO systems, SW intake, CCW lines,...) | B | CCGT, Thermal, RO | GRP Regional On-Call Support Contract Dewatering Servcies (GRP pipe internal and external soil dewatering | 1)Perform a yearly technical evaluation on competency and quality of services 2)Audit Test/Repair tProcedures and equipment which Contractor is using. Fleet Standardization Scope and acceptance criteria | Assure Robust Contigency Plant for Critical GRP pipe leakage | COE/EVP/PGM |  |  |  | Q1
| 1 | GRP Critical Piping (RO systems, SW intake, CCW lines,...) | B | CCGT, Thermal, RO | 1) GRP Pipe Internal Sealing Spare parts - 2) Establish Regional on-call contract (cfr call Hassayn Jan 27th 2023). Lead time spares is minimum 6 weeks 2) Rationalize the GRP ring spares and sealing consumables with each applicable plant across the Fleet |  | Assure Robust Contigency Plant for Critical GRP pipe leakage | COE/EVP/PGM |  |  | 3rd Party (Eco Innovative (pls contact Hassyan Team Maqsood) | Q1
| 2 | Civil Structure | B | CCGT, Thermal, PV, RO, CSP, Wind | Organize Civil Survey on Plant (Flooring , Structures, Groutings, Roof Beams, Building wall/roofs, Roads, Soil Settlement aorund building,...) | Findings wil be ranked and rated in priority as per criticality of the system and area | Assure Civil Integrity / Safety | COE/EVP/PGM | X | monitor and/or consolidate | CTO Recommended 3rd Parties (SWPC, S&L, ITALO) - | Q4
| 2 | Civil Structure | B | CCGT, Thermal, PV, RO, CSP, Wind | Remedial Execution of all Critical Prioirty-1 Observations | Findings wil be ranked and rated in priority as per criticality of the system and area | Assure Civil Integrity / Safety | EVP/PGM | X | monitor and/or consolidate | CTO Recommended 3rd Parties (SWPC, S&L, ITALO) - | Q4
| 2 | Plant Corrosion Review | B | CCGT, Thermal, PV, RO, CSP, Wind | Organize Corrosion Survey as per Nomac Guideline (incl Plant Structures, Tanks, Equipment , Critical Pipes, Hangers,...) | Findings wil be ranked and rated in priority as per criticality of the system and area | Assure Civil Integrity / Safety | COE/EVP/PGM | X | monitor and/or consolidate | 3rd Party (eg. Jotun) | Q4
| 2 | Plant Corrosion Review | B | CCGT, Thermal, PV, RO, CSP, Wind | Remedial Execution of all Critical Priority-1 Observations | Findings wil be ranked and rated in priority as per criticality of the system and area | Assure Civil Integrity / Safety | EVP/PGM | X | monitor and/or consolidate | 4th Party (eg. Jotun) | Q4
| 2 | Plant Corrosion Review | B | CCGT, Thermal, PV, RO, CSP, Wind | Set Regional Frame Agreement Painting and Coating | 1)Perform a yearly technical evaluation on competency and quality of services 2)Audit Test/Repair tProcedures and equipment which Contractor is using. Fleet Standardization Scope and acceptance criteria |  | COE/EVP/PGM |  |  | 5th Party (eg. Jotun) | Q4
| 2 | Condition Monitoring Program | P | CCGT, Thermal, PV, RO, CSP, Wind | Ensure compliance EPRI PMBD Guideline Implementation , referring to condition monitoring |  |  | EVP/PGM | X | spot check field records (remote) |  | Q3
| 2 | Condition Monitoring Program | C | CCGT, Thermal, PV, RO, CSP, Wind | 1)Ensure that all applicable MPC critical Equipment alerts are monitored, validated and actioned upon by Plant Operations. 2) Awareness of critical signals, alarms and algorithms ) 3)Updating the case management in case of critical alarm |  | 1) Full adoption of MPC 2) Capture of Catches before main degradation/ Failure | EVP/PGM | X | track signed TB sheets | EPRI / Hassyan | Q3
| 1 | SPOF Spares Management | B | CCGT, Thermal, PV, RO, CSP, Wind | Ensure implementation Nomac Corporate SPOF Guideline for critical spare selection (including ISP for new-build) |  | Plant Availabilty and Inventory Optimization | COE/EVP/PGM |  |  |  | Q1
| 1 | SPOF Spares Management | A B | CCGT, Thermal, PV, RO, CSP, Wind | SPOF analysis done per plant + reviewed by PAT and sign off by PGM, EVP , EMO and RD for joint agreement. | 1) summary of business cases for high value USD SPOF might be necessary | Plant Availabilty and Inventory Optimization | COE/EVP/PGM |  |  |  | Q1
| 1 | SPOF Spares Management | A B | CCGT, Thermal, PV, RO, CSP, Wind | Assess and identify Spare Pooling of Critical SPOF (eg. GT bearings AES GT machines) within the Region |  | Plant Availabilty and Inventory Optimization | COE/EVP/PGM |  |  |  | Q1
| 1 | SPOF Spares Management | B | CCGT, Thermal, PV, RO, CSP, Wind | Selected SPOF spares ordered and received on site |  | Plant Availabilty and Inventory Optimization | EVP/PGM |  |  |  | Q1
| 1 | SPOF Spares Management | B | CCGT, Thermal, PV, RO, CSP, Wind | SPOF spares Quantiy identification in SAP MM (re-order MRP Quantity) |  | Plant Availabilty and Inventory Optimization | EVP/PGM |  |  |  | Q1
| 1 | SPOF Spares Management | B | CCGT, Thermal, PV, RO, CSP, Wind | Set and activate Regional Just-In-Time Frame Agreement for consumables/commodities Elec, I&C, Mec consumables |  | Plant Availabilty and Inventory Optimization | EVP/PGM |  |  |  | Q3
| 2 | Technical Frame Agreements - Standardization Outsourced/In-House Competency | B | CCGT, Thermal, PV, RO, CSP, Wind | Implement the Nomac Corporatte Guideline In-house / Outsourced Contracting |  |  | COE/EVP/PGM |  |  |  | Q4
| 2 | Insurance Points (applicable to Plant) | A B | CCGT, Thermal, PV, RO, CSP, Wind | Closure and/or with firm action plan + tentative execution date | Proposed actions shall be discussed and approved in agreement with Insurance Marsh |  | COE/EVP/PGM |  |  |  | Q4
| 2 | SCD Equipment Test Compliance | P | CCGT, Thermal, PV, RO, CSP, Wind | Compliance to Frequency and Scope |  |  | COE/EVP/PGM |  |  |  | Q4

## Scope
Region |  | Plant |  | Persons | Site Time | Generator | Elec Protections (Critical) | Critical Transformers (GSU/UAT/EXC) | Generator CB | UPS/Battery | VFD (MV systems) | Storage Tanks | Vessels | PV Transformers | PV Central/String Inverter | HV Cable Sealing Ends | Earthing Survey Reports | GasChromatograph | CSP - SGS and TES Heat Exchangers
AFRICA | Maroc | NOOR 1 | CSP | 1 x person A | 1 day | X | X | X | X | X | X | X | X |  |  | X | X |  | X
AFRICA | Maroc | NOOR 3 | CSP | 1 x person A | 1 day | X | X | X | X | X | X | X | X |  |  | X | X |  | X
AFRICA | Maroc | NOOR 2 | CSP | 1 x person A | 1 day | X | X | X | X | X | X | X | X |  |  | X | X |  | X
AFRICA | Maroc | NOOR IV | PV | 1 x person A | 1 day |  | X | X | X | X |  |  |  | X | X | X | X
GULF | Bahrain | AL DUR II | CCGT/RO | 1 x person B | 1 day | X | X | X | X | X | X | X | X |  |  | X | X | X
GULF | KSA | QIPP | CCGT | 1 x person B | 1 day | X | X | X | X | X | X | X | X |  |  | X | X | X
GULF | KSA | SAKAKA | PV | 1 x person B | 1 day |  | X | X |  | X |  |  |  | X | X | X | X
GULF | KSA | Jubail 3A | RO | 1 x person B | 1 day |  | X | X |  | X | X | X | X |  |  | X | X
MEA | UAE | HSYN | Thermal | 1 x person C | 1 day | X | X | X | X | X | X | X | X |  |  | X | X
MEA | UAE | TAWEELAH | RO/PV | 1 x person C | 1 day |  | X | X |  | X | X | X | X | X | X | X | X
MEA | UAE | UAQ | RO | 1 x person C | 1 day |  | X | X |  | X | X | X | X |  |  | X | X
MEA | UAE | NE1 (DEWA IV) | CSP/PV | 1 x person C | 1 day | X | X | X | X | X | X | X | X | X | X | X | X
MEA | UAE | SALALAH I | CCGT | 1 x person C | 1 day | X | X | X | X | X | X | X | X |  |  | X | X | X
MEA | UAE | SALALAH II | CCGT | 1 x person C | 1 day | X | X | X | X | X | X | X | X |  |  | X | X | X
MEA | UAE | IBRI I & II | CCGT | 1 x person C | 1 day | X | X | X | X | X | X | X | X |  |  | X | X | X
MEA | UAE | SHUAR III | CCGT | 1 x person C | 1 day | X | X | X | X | X | X | X | X |  |  | X | X | X
MEA | UAE | BARKA | RO | 1 x person C | 1 day |  | X | X |  | X | X | X | X |  |  | X | X
MEA | UAE | DEWA V | PV | 1 x person C | 1 day |  | X | X |  | X |  |  |  | X | X | X | X
MEA | UAE | SHUAA I | PV | 1 x person C | 1 day |  | X | X |  | X |  |  |  | X | X | X | X
MEA | UAE | KIPP | CCGT | 1 x person C | 1 day | X | X | X | X | X | X | X | X |  |  | X | X | X
RED SEA | KSA | SWIPP | Thermal/RO | 1 x person D | 1 day | X | X | X | X | X | X | X | X |  |  | X | X
RED SEA | KSA | SIWEP | RO | 1 x person D | 1 day |  | X | X |  | X | X | X | X |  |  | X | X
RED SEA | KSA | ROMCO | Thermal | 1 x person D | 1 day | X | X | X | X | X | X | X | X |  |  | X | X
RED SEA | KSA | R2IPP | CCGT | 1 x person D | 1 day | X | X | X | X | X | X | X | X |  |  | X | X | X
RED SEA | KSA | RABIGH 3 IWP | RO | 1 x person D | 1 day |  | X | X |  | X | X | X | X |  |  | X | X
RED SEA | KSA | SQWP | Thermal/RO | 1 x person D | 1 day | X | X | X | X | X | X | X | X |  |  | X | X
RED SEA | KSA | WDEC | RO | 1 x person D | 1 day |  | X | X |  | X | X | X | X |  |  | X | X
RED SEA | KSA | RPC | Thermal/RO | 1 x person D | 1 day | X | X | X | X | X | X | X | X |  |  | X | X
inhouse
AFRICA |  | BENBAN 1 | PV | 1 |  | in-house
AFRICA |  | BENBAN 2 | PV | 1 |  | in-house
AFRICA |  | BENBAN 3 | PV | 1 |  | in-house
AFRICA |  | KHWF | Wind | 1 |  | in-house
AFRICA |  | BOOKPORT | CSP | 1 |  | in-house
AFRICA |  | NOOR IV Lyn | PV | 1 |  | in-house
AFRICA |  | NOOR IV Bzd | PV | 1 |  | in-house
AFRICA |  | REDSTONE | CSP |  |  | in-house
AFRICA |  | KOMOBO | PV |  |  | in-house
GULF |  | SUDAIR PV |  |  |  | in-house
MEA | UAE | SIRDARYA I |  |  |  | in-house

## SCD equip reviewed by EPRI
S&SC Integrity/Performance Assurance Requirements
S&SC Grouping (Service/Operating Parameters) |  | Acceptance Criteria | Assurance Task | In-House / 3rd Party | Frequency | Reference (Regulation, Standard) | Remarks
MECHANICAL | Pressure Relief Valves | 1)No leaks from valve body or connections 2)not be subject to adverse levels of vibration/fatigue. 3)no severe external corrosion, mechanical damage and 4)the condition of any protective coating shall not have deteriorated 5) Valves are on-line and not isolated or by-passed (continuous) | Visual Inspection | In-house | Monthly | API 576
|  |  | Trevi Testing (HP/IP Steam and Feedwater > 1.7 bar) Seat Leakage Test Off-line internal overhaul & Inspection Pre and post overhaul/inspection pop tests confirm operation within 130% of the correct set point. | 3rd Party | Annual | API 510 API 576
| Hangers & Supports | 1)absence of: * Topped out or bottomed out supports * Indicated position not within design range * Bent rigid rod supports * Bent structural steel associated with supports * Corroded or bent spring cans * Loose rod and clamp bolts * Lug weld cracks 2) Survey Position in Hot and Cold Range | visual inspection | 3rd Party | Min every 5 years | ANSI/MSS SP-58
| Pressure Vessels (steam, air, compressed/liquified gas,…) |  | Ultrasonic Thickness Inspection incl: Wall Thickness Corrosion Rate Remaining Life Calculation NDT - Magnetic Particle Inspection (Welds) Ultrasonic Thickness Measurement (HRSG Drums, Pressure Parts etc.) | 3rd Party | 1)External inspection after every 2 years 2)Internal inspection after every 4 years. The frequency can be extended using Risk based Inspection method and assessed by an Pressure Vessel Inspector No hydrostatic test is required unless a defect is found | API 510
| Above Ground Storage Tanks |  | Visual In-Service Inspection external leaks, shell distortions, signs of settlement, corrosion, foundation condition, coatings, insulation systems, operation cathodic protection | In-house | Monthly | API 653
|  |  | Ultra-Sonic Inspection- Tank Shell Tank Grounding system integirty | 3rd Party | External every 5 years | API 653
|  |  | Internal Visual Inspection determine corrosion level bottom tank (man inspection/ robotic/camera) incl. Floor , Shell, Fitting and Roof Support Columns | 3rd Party | Internal every 10 years/one-half of remaining life time | API 653
| High Pressure Piping System | Those risk areas identifed from FAC Program | NDT/Thickness Test | 3th Party | As per recommendation FAC
| HRSG hydro test and certification |  |  | 3rd party | 1-Year or 2-Year (as per local regulation) ????? | to confirm if requierd by local regulation
ENG. STUDIES | HAZOP/SAFOP | Report available/Actions Closed | - | 3rd Party | Design 60% | IEC 61508
|  | Report available/Actions Closed | - | In-house | Review/Validate (1st year of operation) | IEC 61508
|  | Report available/Actions Closed |  | 3rd Party | once in 5 years | IEC 61508
| Arc Flash Study | Report available/Actions Closed |  | 3rd Party | Before handover inc Labels & PPE | NFPA 70E
|  | Report available - Arc Flash measurements/PPE in place |  | In-house | Review/Validate (1st year of operation) | NFPA 70E
|  | Report available - Arc Flash measurements/PPE in place |  | 3rd Party | Every 5 years or whenever there is a significant change in the electrical system | NFPA 70E
ELECTRICAL | Grounding and Lightning Survey | <5 ohms (LV) <1 ohm (HV) [IEEE advised, minimum local regulations to be complied] | Fall-of-potential Check Resistance of Each Earthing Electrode, installed on Plant site, by fall-of-potential method (disconnect the electrode during test) | 3rd Party | Every 2 years | IEEE 80
|  | 1) Visual inspection - no damage, corrosion fixings, fastenings, joints,.. 2) Continuity of the earth conductors to the electrodes 3) no considerable leakage currents in the earth conductors checks of the presence, appropriate redundancy, suitability and visible condition of earthing conductors, connections, surface layer materials and connected equipment | Visual Inspection and Continuity Testing 1) Overall Visual inspection (corrosion, overheating) 2) Continuity Check of all earthing connections (any presence of high resistant joint) 3) Measurement Current in Electrodes | In-house | Every 3 years | IEEE 80
| Generator Rotor Earth Fault Relay | 1) Healthiness of the relay (display, leds,…) 2) No rotor fault standing alarm in the DCS [ to be confirmed before carbon brush maintenance] | Earth Fault Relay Validation | In-house | Monthly | EPRI
|  | 1) Confirmation of the settings as per OEM 2) Confirmation of Alarm and Trip functionality | Earth Fault Relay - Simulation of stage 1 (alarm) and stage 2 (trip) | In-house | Annual | EPRI
| Stationary Battery Test (Vented NiCd type/Lead Acid Type) |  | Capacity Test | 3rd Party | 5 yearly | EPRI
| Stationary Battery Test (VRLA type) |  | Capacity Test | 3rd Party | Annual | EPRI
| Emergency Buttons |  |  | in-house | Annual | EPRI
FIRE DETECTION/FIGHTING SYSTEM | Fire Pump (Electric, Diesel, SW fire pump) | as per Corporate Procedure Operational Run (no-flow) for minimum 30 min Test auto-operation | no-flow test /electric motor–driven fire pumps | In-house | Monthly | NFPA 25
|  | as per Corporate Procedure Operational Run (no flow) for minimum 10 min Test auto-operation | no-flow test/engine -driven fire pumps | In-house | Weekly | NFPA 25
|  | as per Corporate Procedure minimum 3 performance points (0%, 100%, 150%) plotting graph + max 5% degradation | Fire Pump Performance Test | 3rd Party | Annual | NFPA 25
| Fire Detectors (Smoke, Heat, Flame, Gas) | Simulation successful, detectors reliable and available | 1) Simulation with fire Test Kit 1) Confirm alarm with 1 detector 2) Confirm Fire Alarm with minimum 2 detectors 3) Confirm Solenoid Valve of fire suppression system (with minimum 2 detectors) | 3rd party | Annual | NFPA 72
| Hydrogen Detector (eg. Battery) | Calibration complete and alarms received | 1) Calibration 2) Simulate and confirm alarms | In-house | Annual (to be confirmed with OEM) | as per OEM
| CH4 Gas Detector | Calibration complete and alarms received | 1) Calibration 2) Simulate and confirm alarms | In-house | Annual (to be confirmed with OEM) | as per OEM
| Fire Alarm System |  | 1) Battery Healthiness 2) Verification of annunciation system | In-house | 6- monthly
| Fire Sprinklers - Transformers with Fixed Water Spray or Water Mist Type. | 1) Visual Check - Uniform Spray Pattern which covers the whole transformer body (including Cable compartment) 2) Functional Test of the device which triggers the water release (eg. heat detector) 3) Functional Test of the device which triggers the transformer trip (if applicable) 4) Water is delivered to the discharge nozzles 5) Nozzles are free of debris , no blocking 7) Confirmation alarm in DCS 8) Sufficient Drainage 9) Video of each Spray Test to be recorded | Visual Check Functional Test (Trip Test with Spray Test) | In-house | Annual | NFPA 750 NFPA 25
| Fire Suprression Systems (FM200/CO2)- People Occupancy rooms (eg. FM200 control room, CO2 electrical room,…) | 1)Releasing panel is powered and is free of supervisory, trouble or alarm conditions 2) Manual controls are unobstructed. 3)No damage 4) Pressure gauges are in the operable range 5) No modification on the protected equipment/hazard 6) No deficiencies, all corrected | Visual | In-house | Monthly | NFPA 25 NFPA 2001
|  | Loss of pressure less than 5% No damage (containers, hoses etc.) | Visual | In-house | 6-Monthly | NFPA 25 NFPA 2001
|  | No damage Hold pressure No leakage No hose damage | Visual Strength Tests Calibration Trip test without releasing the agent | 3rd Party | Annual | NFPA 25 NFPA 2001
|  |  | Enclosure inspection | 3rd party In-house | NFPA 2001 requires the enclosure to be inspected at least once a year, unless you have a documented administrative control program that addresses barrier integrity. | NFPA 25 NFPA 2001
| Fire Suppresion System- Foam system |  | visual check | In-House | Monthy | NFPA 11
|  | manufacturer specification | Foam proportoning system Foam Concentration Test Trip test without releasing the agent | 3rd party | Annual | NFPA 11
| Deluge System (incl. dry-pip valves, preaction valves) |  | Visual Check | In-House | Monthly | NFPA 13 Parag 7.3
|  |  | Functional Test (Trip Test and Flow Test) | In-House | Annual | NFPA 13 Parag 7.4
| Hydrants |  | Inspect and Clean Flush Lubricate | In-House | Annual
|  | NFPA recommends that a residual pressure of 20 psi be maintained in fire hydrants for them to be effective for firefighting | Flow Test | 3rd party | 5-Year | NFPA 291
| GT Fan Door Test | NFPA 2001 requires that a minimum concentration of 85 percent of the adjusted minimum design concentration be held at the highest level of combustibles for a minimum of 10 minutes. A door fan test assures the room can hold the clean agent for this required period of time |  | 3rd party | Baseline + after dissambly /re-assembly GT enclosures (outage) | NFPA 2001
| Fire Extinguishers o DCP Type Extinguisher for Class ‘A’ Fires (Ordinary materials for example wood, paper etc.). o CO2 Type Extinguisher for Class ‘C’ Fires (Electrical for example motor, panel, wiring etc.). o Foam Type Extinguisher for Class ‘B’ Fires (flammable liquids for example paint, grease, oil etc.). | Inspect each extinguisher for:  Proper location  Accessibility  Seals not broken  Pressure gage in operable range (if provided)  Physical condition  Hydro-Test Date | Visual inspection | in-house | monthly | OSHA [29 CFR 1910.157(e)(2) NFPA 10; 7.2.2
|  |  | external maintenance examination (inclu. Weighing) | 3rd Party | Annual | OSHA 29 CFR 1910.157(e)(3) NFPA 10; 7.2.2
| Nonrechargeable Fire Extinguishers |  | Remove from service | 3rd Party | 12-years | NFPA 10; 7.3.1.2
| Halon, dry chemical (powder), and stored pressure Fire extinguishers (not including pressurized water and CO2.) |  | Hydrostatically Test or replace | 3rd Party | 12-years | NFPA 10; 7.3.1.2
| Carbon Dioxide & Pressurized Water Fire Extinghuishers |  | Hydrostatically test and perform maintenance or replace | 3rd Party | 5-Years | NFPA 10; 7.3.1.1
| Fire Hose Reel /Foam Hose Reel, and Cabinets / Boxes SCBA |  | Visual Inspection | In-house | Monthly
| Fire Hoses |  | visual inspection 1) removing the hose from the rack and unrolling 2) checking the hose, couplings, and nozzle for debris, mildew, rotting, or damage by chemicals, burns, cuts, abrasions, or pests | In-house | Annual | NFPA 25
|  |  | Pressure Test | 3rd Party | every three years, with the first time being 5 years after the manufacturing date. | NFPA 25
| Manual Call Points |  |  | in-house | Yearly
| ll Lifting Accessories:  Chains and wire ropes  Rings, links, hooks, shackles, eyebolts, swivels, blocks, snatch blocks | SWL and ID No wear, elangation, damages, bending, twist/knotted, nicks/gauges, cracks, distortion, corrosion, pitting No heat damage No chemical exposure No broken wires Hook openings not more than 10% | Visual and Functional Test | In-house | Before every use 3- Monthly | EN 15011 ISO22915-2 EN 13157 EN 14492-2 | Identification: 1) All Lifting Gear shall be uniquely defined by a serial number which will be physically attached or stamped on the lifting equipment. Safe Working Load and next testing due date shall be indicated 2) On multi leg slings check that the Safe Working Load (SWL) will be marked for the respective sling angle. e.g. two SWL for the same sling: 10 ton at 0 to 90 degrees and 8 ton from 90 to 120 degrees. 3)Tested equipment will be indicated by a different color code. The color code will be linked to the calendar year. Testing: 4) Six Monthly, all the lifting gears which are in direct use or contact with plant employees shall be inspected and certified by authorize party 5) Lifting gear which is not load tested shall be kept in a sealed container and shall not be used on site. 6) Three Monthly routine visual inspections of all lifting gear shall be performed by the Plant O&M (incl: visual inspection, clean and lubricate)
|  |  | SWL inspection - 100% SWL testing On initial supply  After substantial alteration or Major repair adding colour band | 3rd party | 6 monthly
LIFTING EQUIPMENT/TOOLS | Lifting Equipment:  Pedestal cranes, mobile cranes, forklifts, tower cranes  Overhead travelling cranes, wall / pillar cranes, derricks  Winches, hoist (air and electric), crabs, Telfer hoist, powered working Platforms, vehicle lifts or hoists etc.  Mobile or movable jacks and associated “Lifting Equipment” |  | Visual and Functional Test | In-house | 3 monthly and Before every use | EN 15011 ISO22915-2 EN 13157 EN 14492-2
|  |  | Proof Load Test 125% SWL (normally 125% of the Safe Working Load or otherwise stated in the regulations) (static load test under a load of 1.25 times crane capacity + dynamic load test under a load of 1.10 times crane capacity + deflection measurement + brake slip) | 3rd Party | 1)On initial supply 2)Every four (4) years 3)After reinstallation, substantial alteration or major repair 4) Before every major outage
| Chain Blocks, tirfors, pull lifts, trolleys |  | Visual and Functional Test | In-house | 3 monthly and Before every use
|  |  | Visual Inspection Functional and Integrity Test SWL Inspection - 100% SWL testing Lifting gear which is not load tested shall be kept in a sealed container and shall not be used on site. (key control with Operations) | 3rd Party | 6-Monthly | EN 13155 EN 12385 En 1492 EN 818 BS 4278
|  |  | Proof Load Testing 125% SWL | 3rd party | 1)On initial supply 2)Every four (4) years 3)After reinstallation, substantial alteration or major repair 4) Before every major outage
| Escalators |  | SWL Inspection - 100% SWL testing | 3rd party | Every 6 months
|  |  | Proof Load Testing 125% SWL | 3rd party | On initial supply Every one (1) year